Please Note:

This template is intended for educational purposes only, without any express or implied warranty of any kind, including warranties of accuracy, completeness, or fitness for any particular purpose.  You agree that your use of the template is without any recourse whatsoever to PG&E, SCE, SDG&E, or their affiliates. The template is a draft, and anyone using this document should seek the advice of an attorney to develop appropriate ordinance language to meet its jurisdiction’s specific needs, as state and local laws may differ.

This document is the product of a collaborative effort, incorporating input and feedback from several entities and experts based on their collective experiences.

Please contact the Codes and Standards Reach Codes Team at info@LocalEnergyCodes.com for additional information.

This program is funded by California utility customers and administered by Pacific Gas and Electric Company, San Diego Gas & Electric Company (SDG&E®), and Southern California Edison Company under the auspices of the California Public Utilities Commission and in support of the California Energy Commission.

Model Ordinance Language for Air Conditioning Alterations, Replacements and Installations in Existing Single-Family Buildings

Amending the California Green Building Standards Code

Version 1.3

September 24, 2025

Table of Contents

Changes from Prior Versions	1

Scope	1

Introduction	1

Additional Resources	2

Model Ordinance	3

Findings	3

Sample Amendments	4

Other Sample Ordinance Sections	8

# Changes from Prior Versions

Please check LocalEnergyCodes.com to obtain the latest version of this document and supporting materials.

Changes since Version 1.0, April 2025

- Updated links to resources, added new item regarding exceptions to HSC 17958 to list of required findings

- Added performance compliance pathway.

- Redline has been corrected in Section II.

# Scope

- Existing single-family buildings in which an existing air conditioning system is altered or replaced or where an air conditioning system is added, must either install a heat pump as the primary heating source or make other energy conservation improvements.

# Companion Materials

The Local Energy Codes program has developed several resources to support a single family air conditioner replacement (AC to HP) policy, including:

- Local Ordinance Basics

- Local Energy Codes Options and Opportunities

- Single Family Air Conditioner Replacements (AC to HP) Cost-effectiveness Report

  - Single Family AC to HP Study Data

- SF AC to HP Model Ordinance Language (Part 6)

- SF AC to HP Model Staff Report

- SF AC to HP Model Presentation

- State Agency Adoption Resources and Submission Guidance

  - LEC Addendum to 2025 CEC Submittal Instructions

# Introduction

This model ordinance language supports a reach code requiring that a project in a single-family home involving replacement or alteration of an existing air conditioning system or installation of a new air conditioning system in an existing home must either include a heat pump space heater as the primary heating system or install other energy conservation measures. The ordinance is based on the 2025 California Green Building Standards Code (CALGreen) Section A4.204 and includes references to the 2025 California Energy Code and appendices.  See LocalEnergyCodes.com for a version amending the California Energy Code.

Amendments to the State Code appear in strikeouts (deletions) and underlines (additions). Such amendments require that the governing body of the local jurisdiction make express findings, including a CEQA determination, and cite the authorities used to adopt the ordinance. Refer to the Guide for Local Amendments to Building Standards for more information. In addition to the requirements specified in the Guide, the California Energy Commission requires that the findings include a statement to the effect that the local governmental agency’s governing body has, at a public meeting, adopted its determination that the standards are cost-effective.

This initial version of the model reach code amends the California Green Building Standards Code (Title 24, Part 11) and, by reference, the California Energy Code (Title 24, Part 6). However, jurisdictions should consider amending the Energy Code directly to better align the requirements with the CALGreen scope as revised. Contact the Local Energy Codes program for assistance with drafting the requirements in the Energy Code. Amendments to the Energy Code must be approved by the California Energy Commission (CEC).  All amendments to the Building Code must be filed with the California Building Standards Commission.

Jurisdictions may wish to modify elements of the ordinance, such as those marked with the text “[Optional]”.  When modifying the language, ensure all references are maintained and that the ordinance still meets the State requirements.

The headings, footnotes and instructions (in blue) are for staff reference and should be removed from the final ordinance.

The draft ordinance text is provided as an example only. Jurisdictions should be aware that there have been legal challenges to policies that prohibit the installation of gas appliances, and while this policy is quite different, there is a risk that it could also be challenged; consultation with the city/county attorney is recommended. Ensure all ordinance materials are reviewed and verified by relevant jurisdiction staff and the city/county attorney.

# Model Ordinance

ORDINANCE AMENDING THE [CITY/COUNTY OF JURISDICTION] BUILDING CODE TO REQUIRE ENERGY CONSERVATION MEASURES FOR AIR CONDITIONER ALTERATIONS, REPLACEMENTS AND INSTALLATIONS IN EXISTING SINGLE-FAMILY BUILDINGS

DELETE ALL BLUE TEXT

## Findings

Amendments to the State Building Code require jurisdictions to make certain express findings; additional findings are required to support amendments to the State Energy Code. Refer to the CBSC Guide for Local Amendments of Building Standards for more information. Required findings include:

- A declaration of the authorities granted by the State to the jurisdiction to amend the code, which include:

  - Health and Safety Code sections 17958.7 and 18941.5

  - Public Resources Code Section 25402.1(h)(2)

  - Section 10-106 of the California Code of Regulations, Title 24, Part 1

- A determination that the amendments are reasonably necessary to address local climatic, geological, or topographical conditions

- A determination that the proposed standards are cost-effective and a reference to the supporting analysis

- A declaration that the jurisdiction has at a public meeting, adopted its determination that the standards are cost-effective

- A determination that the proposed standards are more stringent than the State Energy Code and that they will require buildings to be designed to consume less energy than permitted by the State Energy Code

- Any findings, determinations, declarations, or reports, including any negative declaration or environmental impact report, required pursuant to the California Environmental Quality Act

- Findings to support adoption under exceptions to Section 17958 of the Health and Safety Code (AB130).

  - As applicable, explain how the ordinance is necessary “to align with a general plan approved on or before June 10, 2025, and that permits mixed-fuel residential construction consistent with federal law while also incentivizing all-electric construction as part of an adopted greenhouse gas emissions reduction strategy.”

  - As applicable, explain how  “the changes or modifications are substantially equivalent to changes or modifications that were previously filed by the governing body of the city or county and were in effect as of September 30, 2025.”

## Sample Amendments

Chapter [cite local code section] of the [local jurisdiction municipal/county code], adoption of the 2025 California Green Building Standards Code, Title 24, Part 11, is hereby amended to add the following sections as mandatory.

A4.204.1 Energy Efficiency. Alterations to existing residential buildings shall comply with Sections A4.204.1.1 and A4.204.1.2.

A4.204.1.1 Altered Space-Conditioning System Serving Existing Single-Family Dwelling Units – Mechanical Cooling. When a space-conditioning system serving an existing single-family dwelling unit is altered in climate zones 1 through 14 and 16 by installation or replacement of an air conditioner, the altered system shall comply with either a, b, or c below in addition to the requirements for installation specified by Title 24, Part 6, Sections 150.2(b)1E and 150.2(b)1F:

a.	A heat pump shall be the primary heating source and sized according to the system selection requirements specified by Title 24, Part 6 of Section 150.0(h)5. Supplemental heating may be provided by an existing gas furnace or existing electric resistance heating as specified in Title 24, Part 6, Sections 150.0(h)7 and 150.0(i); or

b.	An air conditioner shall meet the following all the requirements in either subsection I or II below:

I.	Systems with Existing Duct Distribution Systems:

I. 	R-8 duct insulation for ducts located in unconditioned space; and

A.	II. The duct system measured air leakage shall be equal to or less than 510 percent of the system air handler airflow as confirmed through field verification and diagnostic testing, per the requirements in Title 24, Part 6, Reference Residential Appendix Section RA3.1.4.3.1; and

Exception 1 to A4.204.1.1bIA. If it is not possible to meet the duct sealing requirements, all accessible leaks shall be sealed and verified through a visual inspection and a smoke test by a certified ECC-Rater utilizing the methods specified in Reference Residential Appendix Section RA3.1.4.3.5.

Exception 2 to A4.204.1.1bIA: Existing duct systems, constructed, insulated or sealed with asbestos.

B.	III. Demonstrate, in every control mode, airflow greater than or equal to 400 300 CFM per ton of nominal cooling capacity through the return grilles, and an air-handling unit fan efficacy less than or equal to 0.45 W/CFM. The airflow rate and fan efficacy requirements in this section shall be confirmed through field verification and diagnostic testing, following the procedures outlined in Title 24, Part 6, Reference Residential Appendix RA3.3; and

Exception 1 to A4.204.1.1bIB: Systems unable to comply with the minimum airflow rate and system efficacy requirements shall demonstrate compliance by satisfying all of the following:

1.	Following the procedures in Section RA3.3.3.1.5;

2.	Installing a system thermostat that conforms to the specifications in Section 110.12;

3.	For standard ducted systems (without zoning dampers), meet the applicable minimum total return filter grille nominal area requirements in Table 150.0-B or 150.0-C as confirmed by field verification and diagnostic testing in accordance with the procedures in Reference Residential Appendix Sections RA3.1.4.4 and RA3.1.4.5. The design clean-filter pressure drop requirements specified by Section 150.0(m)12D for the system air filter(s) shall conform to the requirements given in Tables 150.0-B and 150.0-C.

Exception 2 to Section A4.204.1.1bIB: Multispeed compressor systems or variable speed compressor systems shall verify air flow (cfm/ton) and fan efficacy (Watt/cfm) for system operation at the maximum compressor speed and the maximum air handler fan speed.

Exception 3 to Section A4.204.1.1bIB: Gas furnace air-handling units manufactured prior to July 3, 2019 shall comply with a fan efficacy value less than or equal to 0.58 W/cfm as confirmed by field verification and diagnostic testing in accordance with the procedures given in Reference Residential Appendix RA3.3.

C.	IV. In all climate zones, refrigerant charge verification requirements shall meet the requirements in Title 24, Part 6 Section 150.2(b)1Fiib, including the minimum airflow rate specified in Section 150.2(b)1Fiia; and

D.	V. Vented attics shall have insulation installed to achieve a U-factor of 0.020 or insulation installed at the ceiling level shall result in an insulated thermal resistance of R-49 or greater for the insulation alone; luminaires not rated for insulation contact must be replaced or retrofitted with a fireproof cover that allows for insulation to be installed directly over the cover; and

Exception 1 to Section A4.204.1.1(b)ID: Dwelling units with at least R-38 existing insulation installed at the ceiling level.

Exception 2 to Section A4.204.1.1(b)ID: Dwelling units where the alteration would directly cause the disturbance of asbestos unless the alteration is made in conjunction with asbestos abatement.

Exception 3 to Section A4.204.1.1(b)ID: Dwelling units with knob and tube wiring located in the vented attic.

Exception 4 to Section A4.204.1.1(b)ID: Where the accessible space in the attic is not large enough to accommodate the required R-value, the entire accessible space shall be filled with insulation provided such installation does not violate Section 806.3 of Title 24, Part 2.5.

E.	VI. Air seal all accessible areas of the ceiling plane between the attic and the conditioned space including all joints, penetrations and other openings that are potential sources of air leakage by caulking, gasketing, weather-stripping or otherwise sealing to limit infiltration and exfiltration.

Exception 1 to Section A4.204.1.1bIE: Dwelling units with at least R-38 existing insulation installed at the ceiling level.

Exception 2 to Section A4.204.1.1 bIE: Dwelling units where the alteration would directly cause the disturbance of asbestos unless the alteration is made in conjunction with asbestos abatement.

Exception 3 to Section A4.204.1.1bIE: Dwelling units with atmospherically vented space heating or water heating combustion appliances located inside the pressure boundary of the dwelling unit.

II.	Entirely New or Complete Replacement Duct Systems:

A.	R-8 duct insulation shall be installed for all new ducts located in unconditioned space; and

B.	The total duct system measured air leakage shall be equal to or less than 5 percent of the system air handler airflow as confirmed through field verification and diagnostic testing, per the requirements in Title 24, Part 6, Reference Residential Appendix Section RA3.1.4.3.1; and

C.	Demonstrate, in every control mode, airflow greater than or equal to 350 CFM per ton of nominal cooling capacity through the return grilles, and an air-handling unit fan efficacy less than or equal to 0.35 W/CFM. The airflow rate and fan efficacy requirements in this section shall be confirmed through field verification and diagnostic testing, following the procedures outlined in Title 24, Part 6, Reference Residential Appendix RA3.3; and

D.	 In all climate zones, refrigerant charge verification requirements shall meet the requirements in Title 24, Part 6 Section 150.2(b)1Fiib; and

E.	In Climate Zones 1-4, 6, and 8-16 if the air handler and ducts are located within a vented attic, vented attics shall have insulation installed to achieve a U-factor of 0.020 or insulation installed at the ceiling level shall result in an insulated thermal resistance of R-49 or greater for the insulation alone; luminaires not rated for insulation contact must be replaced or retrofitted with a fireproof cover that allows for insulation to be installed directly over the cover; and

Exception 1 to Section A4.204.1.1bIIE: In Climate Zones 1, 3, and 6, dwelling units with at least R-19 existing insulation installed at the ceiling level.

Exception 2 to Section A4.204.1.1bIIE: Dwelling units where the alteration would directly cause the disturbance of asbestos unless the alteration is made in conjunction with asbestos abatement.

Exception 3 to Section A4.204.1.1bIIE: Dwelling units with knob and tube wiring located in the vented attic.

Exception 4 to Section A4.204.1.1bIIE: Where the accessible space in the attic is not large enough to accommodate the required R-value, the entire accessible space shall be filled with insulation provided such installation does not violate Section 806.3 of Title 24, Part 2.5.

F.	In Climate Zones 2, 4, and 8-16, air seal all accessible areas of the ceiling plane between the attic and the conditioned space including all joints, penetrations and other openings that are potential sources of air leakage by caulking, gasketing, weather-stripping or otherwise sealing to limit infiltration and exfiltration.

Exception 1 to Section A4.204.1.1bIIF: Dwelling units with at least R-19 existing

insulation installed at the ceiling level.

Exception 2 to Section A4.204.1.1bIIF: Dwelling units where the alteration would directly cause the disturbance of asbestos unless the alteration is made in conjunction with asbestos abatement.

Exception 3 to Section A4.204.1.1bIIF: Dwelling units with atmospherically vented space heating or water heating combustion appliances located inside the pressure boundary of the dwelling unit.

c. Performance approach.

The energy budget for alterations is expressed in terms of Long-term System Cost (LSC), and the altered component(s) and any newly installed equipment serving the alteration shall meet the applicable requirements of Subsections A, B, and C below.

A. The altered components shall meet the applicable requirements of Title 24, Part 6, Sections 110.0 through 110.9, Sections 150.0(a) through (l), Sections 150.0(m)1 through 150.0 (m)10, and Sections 150.0(p) through (q). Entirely new or complete replacement mechanical ventilation systems as these terms are used in Section 150.2(b)1L, shall comply with the requirements in Section 150.2(b)1L. Altered mechanical ventilation systems shall comply with the requirements of Section 150.2(b)1M. Entirely new or complete replacement space-conditioning systems, and entirely new or complete replacement duct systems, as these terms are used in Sections 150.2(b)1C and 150.2(b)1Diia, shall comply with the requirements of Sections 150.0(m)12 and 150.0(m)13.

B. The standard design for an altered component shall be the higher efficiency of existing conditions or the requirements stated in Table A4.204.1.1-A . For components not being altered, the standard design shall be based on the existing conditions. When the third party verification option is specified as a requirement, all components proposed for alteration for which the additional credit is taken, must be verified by a certified ECC-rater.

Table A4.204.1.1-A Standard Design for an Altered Component

| Altered Component | Standard Design Without Third Party Verification of Existing Conditions Shall be Based On | Standard Design With Third Party Verification of Existing Conditions Shall be Based On |
| --- | --- | --- |
| Ceiling Insulation, Wall Insulation, and Raised-floor Insulation | The requirements of Sections 150.0(a), (c), and (d). The requirements of Section 150.2(b)1J for altered ceilings and for entirely new or complete replacement duct systems where the air handler and ducts are located within a vented attic. The requirements of Section A4.204.1.1b for alterations which include new or replacement air-cooled air conditioners. | The existing insulation R-value |
| Fenestration | The requirements of Section 150.1(c)3A. | The existing fenestration U-factor and SHGC values as verified. |
| Window Film | The requirements of Section 150.1(c)3A. | The existing fenestration in the alteration shall be based on TABLE 110.6-A and TABLE 110.6-B. |
| Doors | The U-factor of 0.20. The door area shall be the door area of the existing building. | If the proposed U-factor is < 0.20, the standard design shall be based on the existing U-factor value as verified. Otherwise, the standard design shall be based on the U-factor of 0.20. The door area shall be the door area of the existing building. |
| Space-Heating and Space-Cooling Equipment | Table 150.1-A for equipment efficiency requirements; Section 150.2(b)1C for entirely new or complete replacement systems; Section 150.2(b)1F for refrigerant charge verification, airflow, and fan efficacy requirements. Section A4.204.1.1b for new or replacement air-cooled air conditioners | The existing efficiency levels. |
| Air Distribution System – Duct Sealing | The requirements of Sections 150.2(b)1D and 150.2(b)1E | The requirements of Sections 150.2(b)1D and 150.2(b)1E |
| Air Distribution System – Duct Insulation | The proposed efficiency levels. The requirements of Sections 150.2(b)1D, and for new or replacement air-cooled air conditioners, Section A4.204.1.1b. | The existing efficiency levels. |
| Water Heating Systems | The requirements of Section 150.2(b)1Hii | The existing efficiency level. |
| Roofing Products | The requirements of Section 150.2(b)1I. | The requirements of Section 150.2(b)1I |
| All Other Measures | The proposed efficiency levels. | The existing efficiency levels. |

C. The proposed design shall be based on the actual values of the altered components.

Exception 1 to Section A4.204.1.1: Where the capacity of the existing main electrical service panel is insufficient to supply the electrical capacity of a heat pump and where the existing main electrical service panel is sufficient to supply a new or replacement air conditioner, as calculated according to the requirements of California Electrical Code Article 220.83 or Article 220.87. Documentation of electrical load calculations in accordance with Article 220 must be submitted to the enforcement agency prior to permitting for both the heat pump and proposed air conditioner.

Exception 2 to Section A4.204.1.1: Where the required capacity of a heat pump to meet the system selection requirements of Section 150.0(h)5 is greater than or equal to 12,000 Btu/h more than the greater of the required capacity of an air conditioner to meet the design cooling load OR the capacity of the existing air conditioner. Documentation of heating and cooling load calculations in accordance with 150.0(h) must be submitted to the enforcement agency prior to permitting for both the heat pump and proposed air conditioner.

## Other Sample Ordinance Sections

Section 2: CEQA

This ordinance is exempt from CEQA under 15061(b)(3) on the grounds that these standards are more stringent than the State energy standards, there are no reasonably foreseeable adverse impacts and there is no possibility that the activity in question may have a significant effect on the environment.

Section 3: Severability

If any word, phrase, sentence part, section, subsection or other portion of this amendment or any application thereof to any person or circumstance is declared void, unconstitutional, or invalid for any reason, then such word, phrase, sentence, part, section, subsection, or other portion, or the prescribed application thereof, shall be severable, and the remaining provisions of this amendment, and all applications thereof, not having been declared void, unconstitutional or invalid, shall remain in full force and effect.  The [name of governing body] hereby declares that it would have passed this amendment and each section, subsection sentence, clause and phrase of this amendment, irrespective of the fact that any one or more sections, subsection, sentences, clauses or phrases is declared invalid or unconstitutional.

Section 4: Violations

Violation of the requirements of this Chapter shall be considered an infraction of the [jurisdiction Municipal/County Code], punishable by all the sanctions prescribed in [cite local reference to infractions].

Section 5: Effective Date

This ordinance shall become effective as of [DATE], upon approval of the California Energy Commission or upon the date the California Building Standards Commission (CBSC) accepts the ordinance for filing, whichever is later.